# SERIES "FA": SURGE PROTECTIVE DEVICE

# TECHNICAL SPECIFICATION – SYSTEM “T” with DISCONNECT Terminals

# 1.0	GENERAL

The following technical specification describes the requirements of the FA24V, FA30V, FA60V (3 amp high current) Eclips "SPD" Surge Protective Device.  The "SPD" system utilizes multiple bi-directional devices designed to suppress and divert transient voltages and surge currents.  The system shall be designed to provide protection for sensitive electronic devices against the harmful effects of surges, transients and electrical line noise and help eliminate false alarms.  The form factor of the system shall be designed to promote ease of installing the system onto the circuit being protected by the device.

# 2.0	STANDARDS

The SPD shall be designed and manufactured to the following standards:

2.1.	Underwriters Laboratory - UL 497

2.2.	National Electric Code, 1996 (NEC)

2.3.	American National Standard Institute (ANSI)

2.4.	Institute of Electrical and Electronic Engineers (IEEE)

2.5.	National Electrical Manufacturers Association (NEMA)

2.6.	Occupational Safety and Health Administration (including Pub. 81-123)

2.7.	ANSI/IEEE C62.41, Categories A, B and C1

2.8.	ANSI/IEEE C62.45

# 3.0	ENVIRONMENTAL REQUIREMENTS

The "SPD" system shall be designed for operation in the following conditions:

3.1.	Operating Temperature	-40C to 60C

3.2.	Relative Humidity	0 - 95%

3.3.	Operating Altitude	0 - 12,000 Feet

4.0	SUBMITTALS

4.1.	Shop drawings shall include complete with the system’s physical and electrical specification requirements and the manufactures recommended installation requirements.  A line item by line item specification compliance matrix is required in the project submittal drawing package to assist the engineer in the equipment approval process.

# 5.0	ELECTRICAL REQUIREMENTS

5.1.	The transient voltage surge suppression system shall have limited 1 amp for zones to 3-amp for strobes, horns bells, and intelligent loops for nominal current handling when installed in a series configuration.

5.2.	The system voltage shall be  30     VDC or,  60  VDC,    2     Wire plus ground wire.

5.3.	The transient voltage surge suppression system shall be a multi-stage device capable rated to divert 10,000 amps per line safely to ground without causing a false alarm:

5.4.	The maximum response time of the system shall not exceed 5 nanosecond due to the sensitive nature of the protected load.  Suppression topology shall be a hybrid platform consisting of Silicon Avalanche Diodes (SAD),  two three-ohm Coil Inductors, and Metal Oxide Varistors (MOV).  Systems that do not contain Silicon Avalanche Diodes are unacceptable.

5.5.	The system shall be provided with a Two Filtering System capable of managing noise levels produced by electro-magnetic interference and radio frequency interference that can cause a false alarm.

5.6.	The system's filtering mode shall provide in line series Circuit Design with a capacitance of 250 pf.

5.7.	The lines protected, Class A (4), Class B (2).

5.8.	As assigned by UL, the Clamping Voltage values shall be no greater than the values listed below:

# Pass Voltage tested to ANSI/IEEE B3 Impulse*

Pathway	24V	60V

Line-Ground	35 Volts peak	 90 Volts peak

*This type of voltage configurations will help eliminate false alarms

# 6.0	SURGE PROTECTION ELEMENTS

6.1.	The transient voltage surge suppression system shall consist of a hybrid technology consisting of multiple SAD/MOV/Inductor circuits designed to suppress transient voltage and divert excess surge currents. The system shall be designed and UL 497 listed to suppress the surge current per each protection mode of protection as detailed in this specification.

6.2.	Each suppression pathway contains 80kAIC 20 mm Metal Oxide Varistors rated to dissipate 10,000 amperes of surge current each.

6.3.	Each MOV, SAD, and inductor within the system shall be designed to dissipate multiple IEEE C62.41 Category B3/C1 (6 kV, 3 kA) events.

6.4.	The number of MOVs, SAD, and inductors within the system is predicated on the overall surge current rating of the system as specified herein.

7.0	CABINET CONSTRUCTION

7.1.	The system enclosure shall be designed for wall mounting, installed in the panel or in a box with 1/2 inch compression fitting.  The enclosure shall have the following NTE dimensions:   1.5" L, 2" W, and 1" D.

7.2.	The cabinet enclosure shall be NEMA 4X (waterproof and corrosion resistant) and shall be rated for either indoor or outdoor applications.

7.3.	The surge suppressor enclosure shall be made of polycarbonate feature a watertight polycarbonate cover or a polycase box.    System's with opaque heat sink potting materials is required for this specification.

7.4.	The system shall be equipped with interconnection Terminals consisting of 12 gauge screw for copper wire measuring up to 12 gauge maximum.  The manufacturer to assist the electrical contractor in the proper installation of the system shall provide these connectors.

# 8.0	STANDARD MONITORING FEATURES

8.1.	 None, the unit is designed to blow open that will prevent false alarms.  The fire Alarm will provide the monitoring indicating that there is trouble on the line in the event of catastrophic failure.

# 9.0	SYSTEM TESTING AND INSTALLATION

9.1.	The manufacturer shall own and operate a surge simulation system which creates an IEEE C62.41 Category B3/C1 (6 kV, 3 kA) surge event.  Each unit must be tested on this test fixture and results commensurate with the IEEE standards shall be shipped with the SPD system to the job site.

9.2.	A representative from the consulting engineer or the end user shall be welcome to witness test the SPD system(s) at the manufacture.  It shall be the cost of the end user to attend such tests if so desired.

9.3.	The manufacturer shall have a trained Fire Alarm installing representative expert to visit the site to do proper installation of the system to ensure maximum performance.

10.0	SYSTEM WARRANTY

The SPD manufacturer shall warrant the entire system against defective materials and workmanship for a life time following delivery from the manufacturer.  This warranty is in effect as long as the unit is installed in compliance with the manufacturer's owner's/operator's and installation manual, UL listing requirements, and any applicable national or local electrical codes.  Care should be taken in identifying the voltage and current rating and configuration of the surge suppression device to maintain this warranty program.

The manufacturer is required to have a nationwide network of factory trained technicians dedicated to repair and service of this product.  The manufacturer shall have a dedicated 1-800 telephone number for service problems and questions.  This number must be manned 24 hours a day, 365 days a year by a knowledgeable factory employee to ensure prompt response to any emergency situation that may arise. The manufacturer is required to be able to service the equipment on a local basis without the requirement to return the product to the manufacturer for proper repair.

# 11.0	ACCEPTABLE MANUFACTURERS

This specification is based on products manufactured by Professional Technical Systems Inc. and provided by Stormin Protection Products Inc. (888) 471-1038.  Other manufacturers may be acceptable provided they meet the performance requirements of the specification.  Other manufacturers must provide the consulting engineer the following information at least ten days prior to the bid date for review purposes:

11.1.	Complete product literature.

11.2.	Complete copy of a UL 497 file including clamping voltage ratings.

11.3.	Independent test laboratory reports indicating compliance with ANSI/IEEE C62.41 and C62.45 Cat B3/C1 waveform test print out.

11.4.	A line by line specification compliance matrix indicating "comply," "deviate," or "exception" complete with comments for clarification purposes.

11.5.	Warranty certificate in compliance with specification section 9.0.

11.6.	Contact and number of local field service support center applicable to this project.

# END OF SPECIFICATION