PTS 480 3D H "SPD": SURGE PROTECTIVE DEVICE

TECHNICAL SPECIFICATION – SYSTEM “L” W/O DISCONNECT

1.0	GENERAL

The following technical specification describes the requirements of the "SPD" Surge Protective Device.  The "SPD" system utilizes multiple bi-directional devices designed to suppress and divert transient voltages and surge currents.  The system shall be designed to provide protection for sensitive electronic devices against the harmful effects of surges, transients and electrical line noise.  The form factor of the system shall be designed to promote ease of installing the system onto the circuit being protected by the device.

2.0	STANDARDS

The SPD shall be designed and manufactured to the following standards:

2.1.	Underwriters Laboratory - UL 1449 Second Edition & 1283

2.2.	National Electric Code, 1996 (NEC)

2.3.	American National Standard Institute (ANSI)

2.4.	Institute of Electrical and Electronic Engineers (IEEE)

2.5.	National Electrical Manufacturers Association (NEMA)

2.6.	Occupational Safety and Health Administration (including Pub. 81-123)

2.7.	ANSI/IEEE C62.41, Categories A, B and C3

2.8.	ANSI/IEEE C62.45

3.0	ENVIRONMENTAL REQUIREMENTS

The "SPD" system shall be designed for operation in the following conditions:

3.1.	Operating Temperature	-40C to 60C

3.2.	Relative Humidity	0 - 95%

3.3.	Operating Altitude	0 - 12,000 Feet

4.0	SUBMITTALS

4.1.	Shop drawings shall include product information, complete with the system’s physical and electrical specifications requirements and the manufactures recommended installation requirements.  A line item by line item specification compliance matrix is required in the project submittal drawing package to assist the engineer in the equipment approval process.

5.0	ELECTRICAL REQUIREMENTS

5.1.	The transient voltage surge suppression system shall have unlimited nominal current handling when installed in a parallel configuration.

5.2.	The system voltage shall be 480 VAC, ThreePhase Delta, Three Wire plus Ground at 60Hz.

5.3.	The transient voltage surge suppression system shall be a multi-stage device capable rated to divert the following current levels in each of the listed pathways of protection:

(	160K amps, 	Line to Line

(	160K amps, 	Line to Ground

(	300K amps, 	Per Phase Rating

(	300K amps, 	Per System Rating

All SPD systems feature the same level of surge current protection in each mode of protection.

5.4.	The system shall operate over a frequency range of 47 hertz to 63 hertz.

5.5.	As assigned by UL, the Clamping Voltage values shall be no greater than the values listed below:

UL 1449-Second Edition Ratings*

Pathway	480

Line-Line	1260 VAC

Line-Ground	870 VAC

*Consult factory for other voltage configurations

6.0	SURGE PROTECTION ELEMENTS

6.1.	The transient voltage surge suppression system shall consist of a hybrid technology consisting of multiple MOV circuits designed to suppress transient voltage and divert excess surge currents. The system shall be designed and UL 1449-Second Edition listed to suppress the surge current per each protection mode of protection as detailed in this specification.

6.2.	Each suppression pathway contains 200 kAIC fused 40 mm Metal Oxide Varistors rated to dissipate 40,000 amperes of surge current each.

6.3.	Each individual MOV within the system shall be designed to dissipate multiple IEEE C62.41 Category C3 (20 kV, 10 kA) events.

6.4.	The number of MOVs within the system is predicated on the overall surge current rating of the system as specified herein.

7.0	CABINET CONSTRUCTION

7.1.	The system enclosure shall be designed for wall mounting.  The enclosure shall have the following NTE dimensions:   10.75" L, 12.75" W, and 5.5" D.

7.2.	The cabinet enclosure shall be NEMA 4X (waterproof and corrosion resistant) and shall be rated for either indoor or outdoor applications.

7.3.	The cabinet enclosure shall be made of polycarbonate and shall feature a gray watertight polycarbonate cover.  The enclosure is UL listed 514, 61E8 & CSA approved.  The enclosure must also be UL listed-marine rating and weather proof.  System's with opaque potting materials or cavities packed with sand are expressly forbidden via this specification.

7.4.	The system shall be equipped with interconnection leads consisting of stranded copper wire measuring 18" long maximum.  These conductors shall be color-coded by the manufacturer to assist the electrical contractor in the proper installation of the system.

8.0	STANDARD MONITORING FEATURES

8.1.	Each phase protection pathway shall contain an LED (light emitting diode) light for easy viewing on top of the system's cover.  The normal operation of the protection pathway shall provide positive indication utilizing the LED light.  Failure of any of the protection pathway shall provide negative indication utilizing the LED light.   The monitoring system shall indicate the failure of any MOV to ensure the user is aware of the full operability of the surge suppression device.  Systems that do not indicate a suppression failure condition are prohibited.

9.0	SYSTEM TESTING AND INSTALLATION

9.1.	The manufacturer shall own and operate a surge simulation system which creates an IEEE C62.41 Category C3 (20 kV, 10 kA) surge event.  Each unit must be tested on this test fixture and results commensurate with the IEEE and UL 1449 Second Edition standards shall be shipped with the SPD system to the job site.

9.2.	A representative from the consulting engineer or the end user shall be welcome to witness test the SPD system(s) at the manufacture.  It shall be the cost of the end user to attend such tests if so desired.

9.3.	The manufacturer shall have a contracted and trained local representative to visit the site to assist the user in the proper installation of the system to ensure maximum performance.

10.0	SYSTEM WARRANTY

The SPD manufacturer shall have a lifetime warranty for the entire system against defective materials and workmanship following delivery from the manufacturer.  This warranty is in effect as long as the unit is installed in compliance with the manufacturer's owner's/operator's and installation manual, UL listing requirements, and any applicable national or local electrical codes.  Care should be taken in identifying the voltage rating and configuration of the surge suppression device to maintain this warranty program.

The manufacturer is required to have a nationwide network of factory trained technicians dedicated to repair and service of this product.  The manufacturer shall have a dedicated 1-800 telephone number for service problems and questions.  This number must be manned 24 hours a day, 365 days a year by a knowledgeable factory employee to ensure prompt response to any emergency situation that may arise. The manufacturer is required to be able to service the equipment on a local basis without the requirement to return the product to the manufacturer for proper repair.

11.0	ACCEPTABLE MANUFACTURERS

This specification is based on products manufactured by PTS Inc, and distributed by Stormin Protection Products Inc., Florida (888) 471-1038.  Other manufacturers may be acceptable provided they meet the performance requirements of the specification.  Other manufacturers must provide the consulting engineer the following information at least ten days prior to the bid date for review purposes:

11.1.	Complete product literature.

11.2.	Complete copy of a UL 1449 file including clamping voltage ratings.

11.3.	Independent test laboratory reports indicating compliance with ANSI/IEEE C62.41 and C62.45.

11.4.	A line by line specification compliance matrix indicating "comply," "deviate," or "exception" complete with comments for clarification purposes.

11.5.	Warranty certificate in compliance with specification section 9.0.

11.6.	Contact and number of local field service support center applicable to this project.

END OF SPECIFICATION