Metal Box

Polymer Box

Panel Protector / Hardwire / M200/277/480 3Y 2nd Edition

Specifications - Operating:				Dry Contacts

8 3/4

8

Maximum Operating Voltage:				480 Volts AC

Typical Leakage Current:					<5µ amps

Operation Temperature:					- 40 to +85°C

Connectors:							Hardwired

Lines Protected:						L-L, L-G, N-G

Installation Configuration:						Parallel

4

Specifications - Electronic:

6 1/4

Maximum Surge Current (8x20µs):				600,000A total, 200KA per Phase

Maximum Surge Voltage (1.2x50µs):			10,000 Volts

Capacitance:							<2,000 pf

Clamping Voltage:						510 Volts RMS

Clamping Response Time:					<5 nanoseconds

Current:							Non-Load Bearing

Voltage:							Voltage Sensitive

Design:							(3) Thermally Fused Hybrid

Operation Indicators & Audible Alarm			(4) Light Emitting Diode (LED)

Power Dissipation (8x20µs):					102,000,000 Volts Amps

Energy Dissipation:						7600 Joules

UL 1449:							1449 Second Edition

UL and CUL Approved:					United States / Canada

Dimension:							Depth  3 1/2"

Length 8 3/4"(including tabs)

Width  6 1/4"

Weight:							Approximately 7.5 lbs Nema 12 Box

### Pass Voltage Tested to ANSI/IEEE B3 Impulse:	(L-L)1800VoltsPeak(L-G)1000V PK (L-N)1000V Pk(N-G)1000V Pk

Stormin surge suppressors have a Ten Year Product Warranty.  Please see warranty statement for complete product warranty information.

Page13

Click here for Index                       Click here for Page12                             Click here for Page 14

Metal Box

Polymer Box

# E-Clips Panel Protector / Hardwire / 480 3Y/ 2nd Edition

# (Cepter/Carlon Box)

# Specifications - Operating:

### Maximum Operating Voltage:			480 Volts AC

Typical Leakage Current:				<5µ amps

Operation Temperature:				- 0 to +85°C

Connectors:						Hardwired

Lines Protected:					L-L, L-G, N-G, L-G

Installation Configuration:				Parallel

# Specifications - Electronic:

Maximum Surge Current (8x20µs):			300,000 Amps Total

Maximum Surge Voltage (1.2x50µs):		10,000 Volts

Capacitance:						<4,000 pf

Clamping Voltage:					510 Volts RMS

Clamping Response Time:				<5 nanoseconds

Current:						Non Load Bearing

Voltage:						Voltage Sensitive

Design:						Hybrid

Power Dissipation (8x20µs):				51,000,000 Volt Amps

Energy Dissipation:					3800 Joules

UL 1449: 					            1449 Second Edition

UL Recognized Component:

UL 514 Enclosure (Marine/Weather Proof):

USL and CNL Approved:				United States  / Canada

Dimension:						Depth 2.50"

Width 4.750"

Length 5.800"

Tabs ½", Neck ½"

Weight:						Approximately 2 lbs.

E-Clips surge suppressors have a Ten Year Product Warranty.  Please see warranty statement for complete product warranty information.