Signal Control Loop Sensor

Fire Alarm Protectors FA 12V B and 30VB are surge protectors for “B” type zones or loops of either 12-volt or 24-volt. Protectors are 3-stage with primary and secondary protection that will greatly reduce false alarms caused by lightning and will protect the equipment. Units are encapsulated with a heat dissipating epoxy, which greatly enhances component performance.

Specifications for Fire Alarm

Zone Protectors

• Connection:	Terminal Board
• Technology:	Hybrid Circuit
	Multi-Stage Design
	Full Heat sinking
• Response:	< 5 Nanoseconds
• Operating Temperature:	-400C - +850C
• Operating Environment	Weather Proof
• Voltage:	Voltage Sensitive
• Current:	Non Load-Bearing
	No Follow -On Current
• Clamping Point:	15 or 30 or 64 Volts

• Power Dissipation:	2,000,000 Volt Amps /

Line
	4,000,000 Volt Amps /
	Line Pair
• Lines Protected:	l Pair (“B” Zone)

2 Pair (“A” Zone)

• UL 497 listed • Tested to ANSI/IEEE B-3 Impulse

S

Fire Alarm	Class A is 2 Pair, Class B is 1 Pair

FA 12VA		12V”A” Zone Protector - 2 Pair

FA 12V B		12V”B” Zone Protector - 1 Pair

FA30VA		24V”A” Zone Protector - 2 Pair

FA30VB		24V”B” Zone Protector – 1 Pair

FA30VB-BH		24V+ 3 amps ”BH” Bells Horns  - 1Pair

FA60VB		34.8V+”B” Zone Protector -1 Pair

FA60VB-NC		34.8V+ 3amps ”B-NC” Bells Horns  –

1 Pair

.

In-line Series Hybrid Three Stage AC Surge Suppressor

# 120HWCP20CB

This Unique Product is designed to provide superior transient voltage surge protection & noise reduction for Branch Circuits, Fire Alarms, PLC, NC/CNC, Controls, Card Access, Gate Access, Telemetry, (2)units in a 120/120 240 single phase application for PLC or Computer related PC board power supply drawing no more the 20 amps per line.  This unit will eliminate a high degree of noise coming in the AC power, caused by HVAC, Pumps, Motors and other noisy equipment that can cause false alarms especially on Fire Alarm panels, or harmful effects affecting the performance of the PC board.

## Specifications – Operating

Maximum Operating Voltage 	135 Volts

Follow on current			none

Circuit Breaker			20 amps

Connection			In-Line series Hardwired

Operating Temperature		-32to 85 C

Maximum Surge Current		(8 x 20us) 300KVA

Maximum Surge Voltage		(1.2 x50us) 20K Volts

TVSS Device UL File		E121637

UL 1449 RVSS Rating		330 Volts L/N, N/G, L/G

Clamping Point			138 Volts RMS, 198V Peak

Clamping Response Time		<5 nanoseconds

Maximum Line Amperage		20 Amps @120 VAC 45/60Hz

Active Filtering		Dual-Full P-N,N-G Response 1Pico

Three Stage Filter	40dB down-10KHz to 10 Mhz

Power Dissipation (8x 20us)	3000 Joules, or 12,000KVA

Failure Mode		Fails Safe (open) UL 1449 2nd edition

Dimensions		Depth: 2.5”, Width: 4.5” Length 5”

Mounting		(4)  .5” tabs & (2) ½” nipples

Installation		P/N/G(3)wire Line in,(3)wire load out

Weight			Approximately 2.5 Pounds

6000V @ 3000amps 	8 x20 us 220V Peak P/N,

ANS/IEEE Cat. B3	265VPK P/G, 207 VPK N/G

Surge Suppressors